## BoQ Elec
Hook-up items required for Trigen at JPNATC
S. NO. | HOOK UP
A | ELECTRICAL HOOK-UP (SUPPLY)
1 | Additional 01 Number bus coupler for distribution | See BOM | 1
2 | 01 No Incomer and 01 No BUS Coupler panel to be couple with HVAC Panel # 1 at AC Plant | See BOM | 1
3 | 01 No Incomer and 01 No BUS Coupler panel to be couple with HVAC Panel # 2at AC Plant | See BOM | 1
4 | Electrical cables from AC Plant to Generator Control panel | 3.5 C X 400 sqmm | 100 x 2 m | Aluminium Armoured Cable, 1.1 KV grade
5 | Cable tray for above cable | 40 X 300 X 40 mm | 45 x 2 m | MS Fabricated Ladder type Cable Trays, hot dip galvanized, accordance to IS:2629
B | BILL OF MATERIAL FOR INCOMER PANEL (BOM)
1 | 800A, TP, MDO ACB with SR-18G release | 1 |  | L&T/Equivalent
2 | Power factor meter, 3-phase 4-wire, size-144 mm x 144mm | 1 |  | AE/Rishabh/Equivalent
3 | kW meter, 3-phase 4-wire, size- 144 mm x 144 mm | 1 |  | AE/Rishabh/Equivalent
4 | AC Ammeter, size- 96x96 mm, analog type, 0-800 A, CTR - 800/5A | 1 |  | AE/Rishabh/Equivalent
5 | AC Voltmeter, size- 96x96 mm, analog type, 0-500 V | 1 |  | AE/Rishabh/Equivalent
6 | Ammeter selector switch | 1 |  | Salzer/Kaycee/Equivalent
7 | Voltmeter selector switch | 1 |  | Salzer/Kaycee/Equivalent
8 | Current Transformer, CL-1.0, 15VA, CTR- 800/5A | 3 |  | Kappa/AE/Equivalent
9 | Indicating Light, LED Type, Dia-22.5 mm, 240 V AC ofr R, Y B, Breaker ON and Breaker OFF | 5 |  | Esbee/Vaishno/Teknic/Equivalent
10 | Control fuse link with base | 1 set |  | GE/L&T/Equivalent
C | BILL OF MATERIAL FOR BUS COUPLER PANEL
1 | 800A, TP, MDO ACB without release | 1 |  | L&T/Equivalent
2 | Indicating Light, LED Type, Dia-22.5 mm, 240 V AC for Breaker ON and Breaker OFF | 2 |  | Esbee/Vaishno/Teknic/Equivalent