## Ground Floor (hidden)
SUMMARY OF GROUND FLOOR CORRIDOR FRESH AIR PURIFICATION SYSTEM
Supply, installation, testing and commissioning of the following equipment and materials as per Drawings Bill of Quantities
S.No. | Description | Unit | Qty | Unit Rate |  | Final Amount |  | Model | Make
1 | TFA |  |  | Supply | Installation | Supply | Installation
1.1 | Supply,installation, testing & commissioning of Double skin type Ceiling Suspended type Fresh Air Purification System complete with mounting arrangement, extruded aluminium section with 0.8 mm preplasticized/prepainted GI sheet outside and inner sheet,50 mm glass wool slab insulation with thermal break profile, High Efficiency imported EC fan with controller and regulator for fan speed modulation,suitable for 415±10% volts, 50 Hz, 3 phase AC supply, SS bird screen mesh at the inlet, & washable pre-filter G4, coarse filter M5, chemical filter, F7 fine filter & F9 fine filter as per specification, copper cooling coils.
| TFA - 750-1000 CFM, 4TR cooling coil | No | 3 | 371000 | 35000 | 1113000 | 105000 | FAPS - 800 | DRI
| TFA - 600-800 CFM, 3TR cooling coil | No | 2 | 185500 | 17500 | 371000 | 35000 | FAPS - 600 | DRI
| Total for FAPS UNITS |  |  |  |  | 1484000 | 140000
2 | Outdoor Unit
| Supply, installation, testing & commissioning of Outdoor units of 4TR with control panel and remote to integrate with FAPS and to operate FAPS with outdoor unit remote | Nos | 3 | 124000 | 15000 | 372000 | 45000 | As per manufacturer standard | Carrier / Daikin
| Supply, installation, testing & commissioning of Outdoor units of 3TR with control panel and remote to integrate with FAPS and to operate FAPS with outdoor unit remote | Nos | 2 | 62000 | 7500 | 124000 | 15000 | As per manufacturer standard | Carrier / Daikin
2.1 | Refrigerant Piping
| Supply and Laying of Interconnecting copper piping with 6mm thick nitrile rubber insulation ( connect with ahu coil to out door unit) | RM | 200 | 1100 | 260 | 220000 | 52000
2.2 | Supply & installation of set of thermostatic expansion valve for 4TR | Nos | 3 | 950 | 340 | 2850 | 1020
| Supply & installation of set of thermostatic expansion valve for 3TR | Nos | 2 | 475 | 170 | 950 | 340
2.3 | Leak testing with preasure testing of refrigerant system with nitrogen, vacumizing and refrigerant charging in the system. This shall be done for the condensing unit to the cooling coil in AHU for 4TR | Nos | 3 | 14000 | 2500 | 42000 | 7500
| Leak testing with preasure testing of refrigerant system with nitrogen, vacumizing and refrigerant charging in the system. This shall be done for the condensing unit to the cooling coil in AHU for 3TR | Nos | 2 | 7000 | 1250 | 14000 | 2500
2.4 | Supply & installation of rigid UPVC piping duly insulated with 6mm thick closed cell nitrile rubber complete with exposed pipe treatment for exposed pipe only
| 25 mm dia | RM | 100 | 150 | 30 | 15000 | 3000
2.5 | Supply & installation of MS Stand duly painted for Outdoor Units for 4TR | Nos | 3 | 3000 | 600 | 9000 | 1800
| Supply & installation of MS Stand duly painted for Outdoor Units for 3 TR | Nos | 2 | 1500 | 300 | 3000 | 600
| Total for DX UNITS |  |  |  |  | 802800 | 128760
3 | Sheet Metal Work
3.1 | Supply, fabrication and erection of following gauges of G.I ducting standard complete with elbows spliters, supports/suspenders bends, tees etc.,
Round /Rectangular Ducting ( Factory/Site fabricated as per SMACNA standard )
a) | 24 gauge | Sq. Mtrs. | 150 | 750 | 275 | 112500 | 41250 |  | GP Spira
3.2 | Al Powder Coated Grills/Diffuserss | Sq. Mtrs. | 1.3 | 8500 | 1500 | 11050 | 1950 |  | Systemair
| Total for Sheet Metal Works |  |  |  |  | 123550 | 43200
4 | Insulation
4.1 | Duct Acoustic
Supply and providing acoustic insulation of ducts with following thickness of open cell Nitrile Rubber .
a) | 13 mm thick | Sq. Mtrs. | 20 | 1250 | 285 | 25000 | 5700 |  | A-Flex
4.2 | Thermal Insulation
Supply and providing thermal insulation of ducts with following thickness of Closed cell Nitrile Rubber .
| 9mm | Sq. Mtrs. | 175 | 390 | 150 | 68250 | 26250 |  | As per duct manufacturer Standard
| Total for INSULATION |  |  |  |  | 93250 | 31950
5 | Electrical Work
5.1 | Cables
Supplying and laying of XLPE insulated aluminium/copper conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends.
a) | 4 C x 4 Sq. mm cu | Mtrs | 50 | 350 | 180 | 17500 | 9000
b) | 4 C x 1 Sq. mm cu | Mtrs | 100 | 220 | 95 | 22000 | 9500
5.2 | Supply, fixing, testing & commissioning of perforated type pregalvanized GI cable trays without cover of the following sizes excluding fixing arrangements as per specifications.
| 300 mm x 40 x 40 x 2 mm thick | RM | 100 | 950 | 275 | 95000 | 27500
5.3 | Double Earthing G.I continuity conductors between panel boards and equipments as required and as per I.E rules 1956
a) | 25 x 3 mm | RM | 30 | 425 | 75 | 12750 | 2250
b) | 8 SWG GI wire | RM | 100 | 510 | 90 | 51000 | 9000
| Total for Electrical |  |  |  |  | 198250 | 57250
| TOTAL= |  |  |  |  | 2701850 | 401160
| GRAND TOTAL= |  |  |  |  | 3103010
| DISCOUNT = |  |  |  |  | 150000
| TOTAL AFTER DISCOUNT = |  |  |  |  | 2953010 |  | GST Extra @ 18%

## SAF-2
BILL OF QUANTITY FOR AIR PURIFICATION SYSTEM FOR SAF-2 (High Side (Item 1 to 3) and Low side (item 4 to 14)
BUDGETARY COST (as on 19 Aug 2020)
S.No. | Description | Unit | Qty | Unit Rate (in INR.) |  | Final Amount (in INR.) |  | Model | Make
1 | AIR PURIFICATION SYSTEM |  |  | Supply | Installation | Supply | Installation
Supply and installation of Double skin type, horizontal, floor mounted Air Purification System in extruded aluminium section construction with 0.8 mm pre-plasticized / pre-painted GI sheet outside and inner sheet, 50 mm insulation with thermal break profile (glass wool, mineral wool or polurethane foam insulation); High efficiency EC plug fan with controller and regulator for fan speed modulation, suitable for 415±10% volts, 50 Hz, 3 phase AC supply; canopy on the top, bird screen mesh and rain hood at the inlet (outdoor installation); Pre filter(G4), Medium filter(M5 Eurovent certified);), Fine Filter (F7 Eurovent certified);), HEPA Filter (H13 Eurovent certified);) and KMnO4 based Chemical filter ; Dx type cooling coil min 6 row deep; SS condensation tray ; Differential Pressure Switches for measuring the differential across filter to give alarm on 80% clog and fan trip on 100% clogging of filters; Units shall pass air tightness (L2) and filter by-pass leakage (maximum filter installation by-pass leakage of 6% (EN 1886)) shall be tested by the manufacturer; Vibration isolators pad below units; Air Purification Units shall be supplied with DOL starter panel along with Power and Communication cabling from the supplied panel to the Air Purification Unit.
| Air Purification Unit - 2000 CFM, 12 HP Cooling coil, 30mmwg External pressure | No | 1 |  |  | 0 | 0 | As per manufacturer standard | DRI/Edgetech/ Flaktwoods
| Air Purification Unit - 3000 CFM, 18 HP Cooling coil, 30mmwg External pressure | No | 1 |  |  | 0 | 0 | As per manufacturer standard | DRI/Edgetech/ Flaktwoods
2 | Outdoor Unit
| Supply, installation, testing & commissioning of Variable refrigerant volume/ Variable refrigerant flow modular type air-conditioning system suitable for cooling and heating by using variable capacity Inverter based compressors in each Module complete with outdoor units with controller and with accessories & sub assemblies fittings etc. full charging of R-410A refrigerant gas with powder coated casing. Units should have minimum COP of 3.8 as per ASHRAE 90.1, 2016 std. | [6 empty] | As per manufacturer standard | Midea / Daikin /LG/Mitsubishi
| 12 HP | Nos | 1 |  |  | 0 | 0
| 18 HP | Nos | 1 |  |  | 0 | 0
3 | Supply,installation, testing & commissioning of Single skin type Ceiling Suspended type Air Purification Units Recirculation type complete with 0.8 mm prepainted GI sheet outside high Efficiency fan with controller and regulator for fan speed modulation,suitable for 220±10% volts, 50 Hz, 1 phase AC supply, with HEPA (H13) filter. The unit shall be complete with circular duct for suction and discharge along with Al powder caoted supply air grills for SAupply and Suction. Unit shall be complete with power and control wiring, threaded rod, fasteners etc. (Dimension of unit should NOT be more than 815 x 515 x 325 mm - L x W x H) | [7 empty] | PureLiving/ DRI
| Max: 550 CFM , Min 247 CFM | Nos | 17 |  |  | 0 | 0
4 | AHU Kit
| Supply, installation, testing & commissioning of AHU Kit for Integrating outdoor units with APS | [7 empty] | Midea / Daikin /LG
| 12 HP | Nos | 1 |  |  | 0 | 0
| 18 HP | Nos | 1 |  |  | 0 | 0
5 | Refrigerant Piping
| Supplying & Installation of interconnecting following sizes of one end expanded refrigerant copper pipe work of required diameter, insulated with closed cell electrometric nitrile rubber tubular insulation between each set of indoor & outdoor units with outer mechanical protection of fibre glass cloth and starbond coating for all exposed pipes and all external piping shall run in M.S. painted cable tray with cover etc. as reqd. (The final refrigerant pipe sizes shall be as per manufacturer). | [7 empty] | Mandev / Maxflow / Rajco
| 28.8 mm OD (insulation 19 mm) | RM | 30 |  |  | 0 | 0
| 15.8 mm OD (insulation 13 mm) | RM | 30 |  |  | 0 | 0
6 | Leak testing with pressure testing of refrigerant system with nitrogen, vacumizing and refrigerant charging in the system. This shall be done for the condensing unit to the cooling coil for following units:
| 12 HP | Nos | 1 |  |  | 0 | 0
| 18 HP | Nos | 1 |  |  | 0 | 0
7 | Supply & installation of rigid UPVC piping duly insulated with 6mm thick closed cell nitrile rubber complete with exposed pipe treatment for exposed pipe only
| 25 mm dia | RM | 30 |  |  | 0 | 0
8 | Supply & installation of MS Stand duly painted for Outdoor Units
| 12 HP | Nos | 1 |  |  | 0 | 0
| 18 HP | Nos | 1 |  |  | 0 | 0
9 | Sheet Metal Work
| Supply, fabrication, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular ducting as per IS-655 complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc of following gauges:- (Make: SAIL/JINDAL | [7 empty] | GI Sheet : Jindal/Tata/Sail
| 24 G | Sq. Mtrs. | 200 |  |  | 0 | 0
| 22 G | Sq. Mtrs. | 50 |  |  | 0 | 0
10 | Thermal Insulation
| Supplying and fixing of following thickness closed cell Cross linked (class“O”) insulation with wrapping from 7 mile fibre glass cloth and two coat of starbond for UV and water protection | [7 empty] | Insulation : Kflex / Armaflex / Aflex Starbond : Paramount
| 20mm | Sq. Mtrs. | 300 |  |  | 0 | 0
11 | Cables
| Supplying and laying of XLPE insulated aluminium/copper conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends. | [7 empty] | Polycab / Havells / KEI
| 4 C x 10 Sq. mm cu | Mtrs | 20 |  |  | 0 | 0
| 4 C x 6 Sq. mm cu | Mtrs | 20 |  |  | 0 | 0
12 | Supply, installation, testing and commissioning of 3 Core x 1.5 mm2 copper wire in PVC conduit for transmission and remote | Mtrs | 100 |  |  | 0 | 0 |  | Polycab / Havells / KEI
13 | Supply, fixing, testing & commissioning of perforated type pre galvanized GI cable trays with cover of the following sizes:
| 150 mm x 40 x 40 x 2 mm thick | RM | 30 |  |  | 0 | 0
14 | Double Earthing G.I continuity conductors between panel boards and equipments as required and as per I.E rules 1956
| 25 x 3 mm | RM | 50 |  |  | 0 | 0
| 8 SWG GI wire | RM | 140 |  |  | 0 | 0
15 | Annual Maintenance for entire system for 02 years including regular visits for servicing, cleaning, consumables and comprehensive warranty on all parts (shall start after the expiry of one year defect liability/warranty period) | Company to specify the schedule
| TOTAL= |  |  |  |  | 0 | 0
| TOTAL FOR SUPPLY AND INSTALLATION IN INR= |  |  |  |  | 0
GST / VAT Shall be extra as applicable
| TOTAL FOR SUPPLY AND INSTALLATION IN EURO= |  |  |  |  | 0